## Sheet1
IEC 63026:2019 | IEC 60502-2
a) partial discharge test at ambient temperature (see 12.5.3); | a) bending test, followed by a partial discharge test (see 18.2.4 and 18.2.5);
b) tan δ measurement (see 12.5.4);₯₯ this test may be carried out on a different sample, with special test terminations, from that used for the remainder of the sequence of tests; Test is carried out at (rated temp+ 5k to 10k) and nominal voltage tan δ < 10x10-4 | b) tan δ measurement (see 18.2.3 and 18.2.6); Test is carried out at (rated temp and voltage ≥ 2 kV tan δ < 40x10-4
c) heating cycle voltage test (see12.5.5); Natural Cooling time is 16 h | c) heating cycle test, followed by a partial discharge test (see 18.2.7); Natural Cooling time is 3 h
d) partial discharge tests (see 12.5.3) – at ambient temperature and – at high temperature; The tests shall be carried out after the final cycle of item c) above or, alternatively, after the tests in item e) below. | d) impulse test, followed by a voltage test (see 18.2.8);
e) lightning impulse voltage test followed by a power frequency voltage test (see 12.5.6); The conductor temperature shall be maintained within the stated temperature limits for at least 2 h. | e) voltage test for 4 h (see 18.2.9).
f) partial discharge tests, if not previously carried out in item d) above (see 12.5.3);
g) examination of the cable system with cable and accessories on completion of the above tests;
h) the resistivity of the cable semi-conducting screens shall be measured on a separate sample.